## USER INFORMATION TEMPLATE
USER INFORMATION TEMPLATE (Version 1.1) Page 1/5
Intended as a template for the identification of items necessary for the assembly manufacturer which is to be provided by the user.
Characteristics | IEC 61439-1 Reference | Default arrangement (a) | Options listed in this document (b) | User requiremet( c)
Electrical system
Type of system earthing | 5.6, 8.4.3.1, 8.4.3.2.3, 8.6.2, 10.5, 11.4 | Manufacturer’s standard, selected to suit local requirements | TT / TN-C / TN-C-S / IT / TN-S | (See at APPENDIX 6)
Nominal voltage (V) | 3.8.9.1, 5.2.1, 8.5.3 | Local, according to installation conditions | Max 1 000 V AC or 1 500 V DC
Transient overvoltages | 5.2.4, 8.5.3, 9.1, Annex G | Determined by the electrical system | Overvoltage category I / II / III / IV
Temporary overvoltages | 9.1 | Nominal system voltage + 1 200 V | None
Rated frequency ƒn (Hz) | 3.8.12, 5.5, 8.5.3, 10.10.3.1, 10.11.5.4 | According to local installation conditions | DC/50 Hz/60 Hz
Additional on-site testing requirements: wiring, operational performance and function | 11.10 | Manufacturer’s standard, according to application | None
Short-circuit withstand capability
Prospective short-circuit current at supply terminals Icp (kA) | 3.8.7 | Determined by the electrical system | None
Prospective short-circuit current in the neutral conductor | 10.11.5.3.5 | Max. 60 % of phase values | None
Prospective short-circuit current in the protective circuit | 10.11.5.6 | Max. 60 % of phase values | None
SCPD in the incoming functional unit requirement | 9.3.2 | According to local installation conditions | Yes / No
Coordination of short-circuit protective devices including external short-circuit protective device details.) | 9.3.4 | According to local installation conditions | None
Data associated with loads likely to contribute to the short-circuit current | 9.3.2 | No loads likely to make a significant contribution allowed for | None
USER INFORMATION TEMPLATE (Version 1.1) Page 2/5
Characteristics | IEC 61439-1 Reference | Default arrangement (a) | Options listed in this document (b) | User requiremet( c)
Protection against electric shock in accordance with IEC 60364-4-41:2005 and IEC 60364-4- 41:2005/AMD1:2017
Type of protection against electric shock – Basic protection (previously protection against direct contact) | 8.4.2 | Basic protection | According to local installation regulations
Type of protection against electric shock – Fault protection (previously protection against indirect contact) | 8.4.3 | According to local installation conditions | disconnection of supply / Electrical separation / Double or reinforced insulation
Installation environment
Location type | 3.5, 8.1.4, 8.2 | Manufacturer’s standard, according to application | Indoor / outdoor
Protection against ingress of solid foreign bodies and ingress of water | 8.2.2, 8.2.3 | Indoor (enclosed): IP2X Outdoor (min.): IP23 | After removal of removable parts: As for connected position / Reduced protection to manufacturer’s standard | (See at APPENDIX 3)
External mechanical impact (IK code) | 8.2.1, 10.2.6 | None | None
Resistance to UV radiation (applies for outdoor assemblies only unless specified otherwise) | 10.2.4 | Indoor: Not applicable. Outdoor: Temperate climate | None
Resistance to corrosion | 10.2.2 | Normal Indoor/Outdoor arrangements | None
Ambient air temperature – Lower limit | 7.1.1 | Indoor: −5 °C Outdoor: −25 °C | None
Ambient air temperature – Upper limit | 7.1.1 | 40 °C | None
Ambient air temperature – Daily average maximum | 7.1.1, 9.2 | 35 °C | None
Maximum relative humidity | 7.1.1 | Indoor: 95 % at −5°C to +30 °C 70 % at +35 °C 57 % at +40 °C Outdoor: 100 % at −25 °C to +27 °C 60 % at 35 °C 46 % at 40 °C | None
USER INFORMATION TEMPLATE (Version 1.1) Page 3/5
Characteristics | IEC 61439-1 Reference | Default arrangement (a) | Options listed in this document (b) | User requiremet( c)
Installation environment
Pollution degree of the macroenvironment (of the installation environment) | 7.1.2 | Industrial: 3 | 1, 2, 3, 4
Altitude | 7.1.1 | ≤ 2 000 m | None
EMC environment (A or B) | 9.4, 10.12, Annex J | A/B | A/B
Special service conditions (e.g. vibration, exceptional condensation, heavy pollution, corrosive environment, strong electric or magnetic fields, fungus, small creatures, explosion hazards, heavy vibration and shocks, earthquakes) | 7.2, 8.5.4, 9.3.3 Table 7 | No special service conditions | None
Installation method
Type | 3.3, 5.6 | Manufacturer’s standard | Various, e.g. floor-standing / wall-mounted
Stationary/Movable | 3.5 | Stationary | Stationary / movable
Maximum overall dimensions and weight | 5.6, 6.2.1 | Manufacturer’s standard, according to application | None
External conductor type(s) | 8.8 | Manufacturer’s standard | Cable / Busbar Trunking System
Direction(s) of external conductors | 8.8 | Manufacturer’s standard | Top/Bottom/Both
External conductor material | 8.8 | Copper | Copper / aluminium
External line conductor, cross-sections, and terminations | 8.8 | As defined within the standard | None
External protective, neutral, mid-point, PEL, PEM, PEN conductor crosssections, and terminations | 8.8 | As defined within the standard | None
Special terminal identification requirements | 8.8 | Manufacturer’s standard | None
Storage and handling
Maximum dimensions and weight of transport units | 6.2.2, 10.2.5 | Manufacturer’s standard | None
Methods of transport (e.g. forklift, crane) | 6.2.2, 8.1.6 | Manufacturer’s standard | None | (See at APPENDIX 7)
Environmental conditions | 7.3 | As service conditions | None
Packing details | 6.2.2 | Manufacturer’s standard | None
USER INFORMATION TEMPLATE (Version 1.1) Page 4/5
Characteristics | IEC 61439-1 Reference | Default arrangement (a) | Options listed in this document (b) | User requiremet( c)
Operating arrangements
Access to manually operated devices | 8.4 |  | Authorized persons / Ordinary persons
Location of manually operated devices | 8.5.5 | Easily accessible | None
Isolation of load installation equipment items | 8.4.2, 8.4.3.3, 8.4.6.2 | Manufacturer’s standard | Individual / groups / all | (See at APPENDIX 5)
Maintenance and upgrade capabilities
Requirements related to accessibility in service by ordinary persons; requirement to operate devices or change components while the assembly is energized | 8.4.6.1 | Basic protection | None
Requirements related to accessibility for inspection and similar operations | 8.4.6.2.2 | No requirements for accessibility | None
Requirements related to accessibility for maintenance in service by authorized persons | 8.4.6.2.3 | No requirements for accessibility | None
Requirements related to accessibility for extension in service by authorized persons | 8.4.6.2.4 | No requirements for accessibility | None
Method of functional unit’s connection | 8.5.1, 8.5.2 | Manufacturer’s standard | None
Protection against direct contact with hazardous live internal parts during maintenance or upgrade (e.g. functional units, main busbars, distribution busbars) | 8.4 | No requirements for protection during maintenance or upgrade | None | (See at APPENDIX 3&5)
USER INFORMATION TEMPLATE (Version 1.1) Page 5/5
Characteristics | IEC 61439-1 Reference | Default arrangement (a) | Options listed in this document (b) | User requiremet( c)
Current carrying capacity
Maximum total load current to be supplied by the assembly (from which the rated current of the assembly InA (A) will be determined) | 3.8.10.1, 5.3, 8.4.3.2.3, 8.5.3, 8.8, 10.10.2, 10.10.3, 10.11.5, Annex E | Manufacturer’s standard, according to application | None | (See at APPENDIX 8)
Design current Ib and nature of load for each circuit; alternatively, In of the devices and nature of the load (in such cases, the assumed loading factors can be used based on the relevant part of IEC 61439) | 3.8.10.8 | None | None | (See at APPENDIX 8)
Ratio of cross-section of the neutral conductor to line conductors: line conductors up to and including 16 mm2 | 8.6.1 | 100% | None
Ratio of cross-section of the neutral conductor to line conductors: line conductors above 16 mm2 | 8.6.1 | 50 % (min. 16 mm2)
USER INFORMATION
Company Name:............................................
Interested Person : ......................................
Contact Info
E-Mail : ........................................................
Phone : .......................................................
Mobile : .....................................................
PROJECT INFORMATION
Project Name:............................................
Project Number : .....................................
! This template should be fulfill for each iindividua assembly (switchboard).
If there are more than one assembly , please fulfill for each one.
DATE : ......................
(a) In some cases, information declared by the assembly manufacturer may take the place of an agreement.
(b) "None" in this column means that there are no options in the standard other than the default condition or value.
(c) For exceptionally onerous applications, the user may need to specify more stringent requirements to those in the document.
(a) In some cases, information declared by the assembly manufacturer may take the place of an agreement.
(b) "None" in this column means that there are no options in the standard other than the default condition or value.
(c) For exceptionally onerous applications, the user may need to specify more stringent requirements to those in the document.
(a) In some cases, information declared by the assembly manufacturer may take the place of an agreement.
(b) "None" in this column means that there are no options in the standard other than the default condition or value.
(c) For exceptionally onerous applications, the user may need to specify more stringent requirements to those in the document.
(a) In some cases, information declared by the assembly manufacturer may take the place of an agreement.
(b) "None" in this column means that there are no options in the standard other than the default condition or value.
(c) For exceptionally onerous applications, the user may need to specify more stringent requirements to those in the document.
(a) In some cases, information declared by the assembly manufacturer may take the place of an agreement.
(b) "None" in this column means that there are no options in the standard other than the default condition or value.
(c) For exceptionally onerous applications, the user may need to specify more stringent requirements to those in the document.
EQUIPMENT LIST &ELECTRICAL DIAGRAM (Please provide the electrical equipments and electrical diagram if they are determined )
Incoming Unit : ACB , Fixed/Withdrawable , Brand and Model , Circuit(A) / Power(kVA)
Outgoing Units : ACB/MCCB/MCB , Brand and model ,Circuit(A) , RDF (Rated diversity Factor)
Withdrawable Outgoing Units : MCCB/DOL/DSD/Soft Starter , Brand and model , Circuit(A) / Power(kW) , RDF (Rated diversity Factor)
Other Fixed Outgoing Units : MCC,/Soft Starter/ Driver/ PLC , Brand and model , Circuit(A) / Power(kW) , RDF (Rated diversity Factor)
Power Factor Correction : kVA , kW , kVAR
Measurement Equipments : Voltmeter/Ampermeter/ Multimeter/others , Brand and Model